## Página1
Calculation Spreadsheet for the Implementation of Photovoltaic Plants
1st Step - Calculate Average Daily Consumption
| Sequence | Month | kWh consumption
| 1 | January | 9809
| 2 | February | 11190
| 3 | March | 8242 |  | Fill in the fields in yellow to calculate the Average Monthly and Daily Consumption. Note: The period does not necessarily need to be from January to December, but an interval of 1 year, for example: August 2022 to July 2023
| 4 | April | 9487
| 5 | May | 13354
| 6 | June | 7925
| 7 | July | 7782
| 8 | August | 11900
| 9 | September | 11078
| 10 | October | 8273
| 11 | November | 10746
| 12 | December | 10211
| Average Monthly Consumption |  | 9999.75
| Average Daily Consumption |  | 333.325
2nd Step - Identify the Region’s Solar Irradiation
| Solar Irradiation |  | 4.5 |  | Note: The following average values ​​can be used by region in Brazil: (Northeast 5.9) - (Central-West 5.7) - (Southeast 5.6) - (North 5.5) - (South 5. 0) or use websites such as https://www.cresesb.cepel.br/ to obtain solar irradiation through the location of the project.
3rd Step - Choose the Photovoltaic Modules
| Solar panel power |  | 470 |  | Enter the power of the solar panel that will be used, considering size and cost, the higher the power, the fewer panels will be used.
4th Step - Calculate the Quantity. of Required Modules
| Quantity of Automatic Modules |  | 174 |  | Automatic calculation of the necessary quantity of Modules, to cover 100% of Consumption, considering a loss of 10%. |  | Quantity of Manual Modules |  | 180 |  | Manual Calculation of Modules, for units that require excess generation for a future increase in load, or compensation in another consumer unit, considering a loss of 10%.
| Monthly Generation |  | 9936.27 |  |  |  | Monthly Generation |  | 10278.9
| Monthly generation surplus |  | -0.6348% |  |  |  | Monthly generation surplus |  | 2.792%
5th Step - Calculate the Minimum Inverter Power
| Total System Power |  | 81.78 |  | Automatic Calculation of the minimum Inverter Power required to cover 100% of Consumption, considering a tolerance rate of 20% of the Inverter. |  | Total System Power |  | 84.6 |  | Automatic Calculation of the minimum Inverter Power required to cover excess Consumption, considering a tolerance rate of 20% of the Inverter.
| Minimum Inverter Power (20%) |  | 68.15 |  |  |  | Minimum Inverter Power (20%) |  | 70.5
6th Step - Size the Inverters
| Inverter Commercial Power |  | 68.8 |  | Enter the commercial power of the inverter manufacturer next to the calculated minimum power |  | Inverter Commercial Power |  | 178
7th Step - Calculate the Area Required for Installation
| Module Area |  | 2 |  |  |  | Module Area |  | 2
| Total Area |  | 348 |  |  |  | Total Area |  | 360
8th Step - Payback Calculation
| City |  | São Paulo
| Installed Power (kWp) |  | 81.78 | Choose the installed power from step 5
| Power of Solar Plates (W) |  | 470 | Item selected in Step 3
| kWh value ($) |  | 1.12 | Inform the value of the last Electricity bill
| Number of plates |  | 174 | Choose the number of plates in the 4th step
| % Application rate |  | 4
| % Energy Inflation |  | 8
| Module Efficiency Value / Year |  | 0.995
| Installed System Cost |  | 368010
| Price per Watt |  | 4.5
| Generation Estimation |  |  |  | Economy |  | Return on Investment
| Month of Ref. | Solar radiation on the inclined plane (kWh/m²)) | Total Generated (kWh/month) |  | Month of Ref. | Total | Year | Accumulated value generated by the photovoltaic system savings | Savings accumulated by the photovoltaic system savings | Return on Investment
| January | 5.6 | 10991.232 |  | January | 12310.1798 | 1 | 129322.8357 | 129322.8357 | -238687.1643
| February | 5.75 | 11285.64 |  | February | 12639.9168 | 2 | 138970.3193 | 273466.0684 | -94543.9316
| March | 5.09 | 9990.2448 |  | March | 11189.0742 | 3 | 149337.5051 | 433742.2162 | 65732.2162
| April | 4.62 | 9067.7664 |  | April | 10155.8984 | 4 | 160478.083 | 611569.9878 | 243559.9878
| May | 3.79 | 7438.7088 |  | May | 8331.3539 | 5 | 172449.7479 | 808482.5353 | 440472.5353
| June | 3.54 | 6948.0288 |  | June | 7781.7923 | 6 | 185314.4991 | 1026136.336 | 658126.3358
| July | 3.71 | 7281.6912 |  | July | 8155.4941 | 7 | 199138.9608 | 1266320.75 | 898310.75
| August | 4.61 | 9048.1392 |  | August | 10133.9159 | 8 | 213994.7272 | 1530968.307 | 1162958.307
| September | 4.84 | 9499.5648 |  | September | 10639.5126 | 9 | 229958.7339 | 1822165.773 | 1454155.773
| October | 5.48 | 10755.7056 |  | October | 12046.3903 | 10 | 247113.6554 | 2142166.06 | 1774156.06
| November | 5.68 | 11148.2496 |  | November | 12486.0395 | 11 | 265548.3341 | 2493401.036 | 2125391.036
| December | 6.12 | 12011.8464 |  | December | 13453.268 | 12 | 285358.2399 | 2878495.318 | 2510485.318
| Total |  | 115466.8176 |  | Total | 129322.8357 | 13 | 306645.9646 | 3300281.095 | 2932271.095
| Average Monthly Generation |  | 9622.2348 |  |  |  | 14 | 329521.7535 | 3761814.092 | 3393804.092
[7 empty] | 15 | 354104.0763 | 4266390.732 | 3898380.732
[7 empty] | 16 | 380520.2404 | 4817566.602 | 4449556.602
[7 empty] | 17 | 408907.0504 | 5419176.316 | 5051166.316
[7 empty] | 18 | 439411.5163 | 6075354.885 | 5707344.885
[7 empty] | 19 | 472191.6154 | 6790560.696 | 6422550.696
[7 empty] | 20 | 507417.1099 | 7569600.234 | 7201590.234
[7 empty] | 21 | 545270.4264 | 8417654.67 | 8049644.67
[7 empty] | 22 | 585947.6002 | 9340308.457 | 8972298.457
[7 empty] | 23 | 629659.2911 | 10343580.09 | 9975570.086
[7 empty] | 24 | 676631.8742 | 11433955.16 | 11065945.16
[7 empty] | 25 | 727108.6121 | 12618421.98 | 12250411.98